## Schedule A
Section 27 Schedule A: SCHEDULES OF PARTICULARS AND GUARANTEES
80MVA 220/66/22 KV Yna0d1 TRANSMISSION TRANSFORMERS
Required: Purchasers specific requirements
Offered: Guarantees and technical particulars of equipment offered
| Description | Unit | Requirement | Offered
Item | Winding Arrangement |  | Core: Tertiary-Secondary-Primary
1 | Delivery and off-loading
1.1 | Transformer delivered to |  | As per agreed schedule
1.2 | Delivery effected not before |  | As per agreed schedule
1.3 | Off-loaded from transport vehicle by supplier Yes / No |  | Yes
1.4 | Transformer transferred to intended operating position by supplier Yes / No |  | Yes
2 | Erection and oil filling
2.1 | Erected ready for service |  | Erected for acceptance testing and long term storage
2.2 | Erection completed not later than |  | To be determined
2.3 | Place 6 ply Malthoid mat under transformer on plinth |  | Yes
3 | Site details
3.1 | Access to site |  | Road
3.2 | Distance from off-loading position | m | 5
3.3 | Rise or fall to off-loading position | m | 1,5
4 | Operating environment (Indoors/Outdoors)
4.1 | Indoors/Outdoors |  | Outdoors
4.2 | Corrosion protection: | Yes/No | Yes
4.3 | Pollution level: | mm/kV | 31
5 | Type of unit required
5.1 | Number of units required |  | 1
5.2 | Single/ 3-phase |  | 3-phase
5.3 | Auto/ Double wound transformer |  | Auto-Transformer
6 | Rated power
6.1 | Primary |  | 80
6.2 | Secondary (with Tertiary unloaded) | MVA | 80
6.3 | Tertiary (with Primary fully loaded) | MVA | 5
7 | Nominal system voltage "Un" ( Um as per IEC)
7.1 | Primary | kV r.m.s | 220
7.2 | Secondary | kV r.m.s | 66
7.3 | Tertiary | kV r.m.s | 22
"The unit shall be able to run at Um continuosly"
8 | Vector group
8.1 | Type |  | Yna0d1
9 | Tap-changers
9.1 | Type |  | OLTC
10 | Bushing Type
10.1 | RIS(Resin Impreg Synthetics with Silicon Rubber Sheds) Outdoor/Cable boxes |  | RIP(Primary)/ RIS (Secondary&Tertially) Outdoor
12 | Maximum continuous ratings on any tapping with rated cooling: |  | ONAF
12.1 | Primary | MVA | 80
12.2 | Secondary (Tertiary unloaded) | MVA | 80
12.3 | Tertiary (with Primary fully loaded) | MVA | 5
13 | Continuous ratings on any tapping with ONAN cooling
13.1 | Primary | MVA | 48
13.2 | Secondary (Tertiary unloaded) | MVA | 48
13.3 | Tertiary (with Primary fully loaded | MVA | 5
14 | Maximum current density in windings
14.1 | Primary | A/mm² | <4
14.2 | Secondary | A/mm² | <4
14.3 | Tertiary | A/mm² | <4
15 | Geomagnetic induced Currents
15.1 | 10 amps on the neutral for 30 minutes |  | Yes
16 | Short-circuit current that the transformer is designed to withstand, in per unit of r.m.s. rated current
16.1 | Primary | p.u. | Infinite busbar
16.2 | Secondary | p.u. | Infinite busbar
16.3 | Tertiary | kA | 20
17 | No-load loss on principal tapping (Note - No plus tolerance allowed)
17.1 | at 1,00 Un | kW | xxxxxxxxxx
17.2 | at 1,10 Un | kW | xxxxxxxxxx
18 | Core design
18.1 | Manufacturer of core steel |  | xxxxxxxxxx
18.2 | Thickness of core steel | mm | xxxxxxxxxx
18.3 | Core material supplier |  | xxxxxxxxxx
18.4 | Core material type (convetional grain oriented/high permeability/domain refined) |  | xxxxxxxxxx
18.5 | Core material designation (as per IEC 60404) |  | xxxxxxxxxx
18.6 | Core material weight | kg | xxxxxxxxxx
18.7 | Core diameter | mm | xxxxxxxxxx
18.9 | Bolts through core |  | No
18.10 | Number of wound\unwound limbs | no. | xxxxxxxxxx
18.11 | Length of wound/unwound limbs | mm | xxxxxxxxxx
18.12 | Wound limb/inner yoke/outer yoke cross-section (as % of wound limb cross-section) |  | xxxxxxxxxx
18.13 | Cross sectional area of:
18.13.1 | Wound limbs | mm² | xxxxxxxxxx
18.13.2 | Yoke | mm² | xxxxxxxxxx
18.13.3 | Unwound limbs | mm² | xxxxxxxxxx
18.14 | Wound limb diameter | mm | xxxxxxxxxx
18.15 | Wound limb length/pitch/wound limb-unwound limb distance | mm/°/mm | xxxxxxxxxx
18.16 | Distance between core limb centres | mm | xxxxxxxxxx
18.17 | Total core mass | kg | xxxxxxxxxx
18.18 | The design flux density at Un for:
18.18.1 | Inner Yoke | T | ≤1,72
18.18.2 | Outer Yoke | T | ≤1,72
18.18.3 | Wound limbs | T | ≤1,72
18.18.4 | Unwound limbs | T | ≤1,72
18.19 | Volts per turn at the above flux densities |  | xxxxxxxxxx
18.2 | Magnetizing current, at rated frequency, on principal tapping, in percent of rated current at maximum Primary rating
18.8.1 | at 0,90 Un | % | xxxxxxxxxx
18.8.2 | at 1,00 Un | % | xxxxxxxxxx
18.8.3 | at 1,10 Un | % | xxxxxxxxxx
19 | Losses
19.1 | No load loss at rated frequency, on principal tapping, in percent of rated current at maximum Primary rating
19.1.1 | at 0,90 Un | kW | xxxxxxxxxx
19.1.2 | at 1,00 Un | kW | xxxxxxxxxx
19.1.3 | at 1,10 Un | kW | xxxxxxxxxx
19.2 | Load loss (I2R + stray) at 75 °C and at maximum Primary rating with Secondary fully loaded but Tertiary unloaded.
(Note - No plus tolerance allowed)
19.2.1 | On principal tapping | kW | xxxxxxxxxx
19.2.2 | On extreme plus tapping | kW | xxxxxxxxxx
19.2.3 | On extreme minus tapping | kW | xxxxxxxxxx
20 | Input to coolers for maximum rated output in service
20.1 | Cooling Fans
20.1.6 | Make fans |  | Howden Safanco
20.1.7 | Type fans |  | xxxxxxxxxx
20.1.8 | Number of fans |  | xxxxxxxxxx
20.1.1 | Motors |  | Three phase induction motors standard frame design impellers to comply to TRMSC0016 (Krenz, WEG, ABB Spain or GEC SA)
20.1.2 | Total Power | kW | xxxxxxxxxx
20.1.3 | Total Current | A | xxxxxxxxxx
20.1.4 | Motor Voltage | VAC | 400
20.1.5 | Control voltage | VDC | 110
20.2 | Oil pumps |  | N/A
20.2.1 | Make pumps |  | xxxxxxxxxx
20.2.2 | Type pumps |  | xxxxxxxxxx
20.2.3 | Number of pumps
20.2.4 | Total Power | kW | xxxxxxxxxx
20.2.5 | Total Current | A | xxxxxxxxxx
21 | IEC impedance at 75 °C and rated frequency based on maximum rated power of Primary winding |  | IEC
21.1 | Primary/Secondary
21.1.1 | Minimum on any tapping | % | 11%
21.1.2 | On principal tapping | % | xxxxxxxxxx
21.1.3 | Maximum on any tapping | % | 13.75%
21.2 | Primary/Tertiary
21.2.1 | Minimum on any tapping | % | xxxxxxxxxx
21.2.2 | On principal tapping | % | xxxxxxxxxx
21.2.3 | Maximum on any tapping | % | xxxxxxxxxx
21.3 | Secondary/Tertiary
21.3.1 | Minimum on any tapping |  | xxxxxxxxxx
21.3.2 | On principal tapping | % | xxxxxxxxxx
21.3.3 | Maximum on any tapping | % | xxxxxxxxxx
21.4 | Zero sequence impedances in percent of Un2/M |  | As per IEC
21.4.1 | Primary/Secondary
21.4.1.1 | Minimum on any tapping | % | xxxxxxxxxx
21.4.1.2 | On principal tapping | % | xxxxxxxxxx
21.4.1.3 | Maximum on any tapping | % | xxxxxxxxxx
21.4.2 | Primary/ Neutral
21.4.2.1 | Minimum on any tapping | % | xxxxxxxxxx
21.4.2.2 | On principal tapping | % | xxxxxxxxxx
21.4.2.3 | Maximum on any tapping | % | xxxxxxxxxx
21.4.3 | Secondary/ Neutral
21.4.3.1 | Minimum on any tapping | % | xxxxxxxxxx
21.4.3.2 | On principal tapping | % | xxxxxxxxxx
21.4.3.3 | Maximum on any tapping | % | xxxxxxxxxx
22 | Temperature rises at altitude of 1 800 m
22.1 | Top oil | °C | 50
22.2 | Windings (by resistance) | °C | 55
22.3 | Hotspot | °C | 68
22.4 | Percentage of total losses that will be supplied | % | 100
22.5 | Maximum temperature rise for metal surface in contact with oil under any conditions | K | 75
23 | Maximum noise level at no-load with cooling equipment for full load operation in service | dBA | < 70
24 | Winding design
24.1 | Indicate per coil the following:
24.1.1 | Type (i.e. multilayer helix) |  | xxxxxxxxxxx
24.1.2 | Total turns |  | xxxxxxxxxxx
24.1.3 | Turns per disc/layer |  | xxxxxxxxxxx
24.1.4 | Overall dimensions - inside diameter/outside diameter/radial build/overall height | mm | xxxxxxxxxxx
24.1.5 | Conductor type, size, number and configuration |  | xxxxxxxxxxx
24.1.6 | Conductor insulation |  | xxxxxxxxxxx
24.1.7 | Disc/layer insulation |  | xxxxxxxxxxx
24.1.8 | Number and width of support spacers per turn |  | xxxxxxxxxxx
24.1.9 | For disc windings with zig-zag oil flow - number of oil guiding washers |  | xxxxxxxxxxx
24.1.10 | For disc windings with vertical ducts - number and dimensions of vertical ducts |  | xxxxxxxxxxx
24.1.11 | Total conductor mass | kg | xxxxxxxxxxx
24.1.12 | Total conductor covering mass | kg | xxxxxxxxxxx
24.1.13 | Dry insulation mass | kg | xxxxxxxxxxx
25 | Minimum insulation for windings (Provide detailed test plan for evaluation)
25.1 | Impulse withstand test voltage for:
25.1.1 | Primary | kV peak | 950
25.1.2 | Secondary | kV peak | 325
25.1.3 | Tertiary | kV peak | 145
25.1.4 | Neutral | kV peak | 110
25.2 | Sixty-second, separate source
25.2.1 | Primary | kV r.m.s | 38+
25.2.2 | Secondary | kV r.m.s | 95x
25.2.3 | Tertiary | kV r.m.s | 50
25.2.4 | Neutral | kV r.m.s | 38+
25.3 | Induced-overvoltage withstand test voltages
25.3.1 | Primary to earth | kV r.m.s | As per IEC
25.3.2 | Secondary to earth | kV r.m.s | As per IEC
25.4 | Between line terminals
25.4.1 | Primary | kV r.m.s | 460
25.4.2 | Secondary | kV r.m.s | 140
25.4.3 | Test frequency | Hz | As per IEC
25.4.4 | Test duration | sec | As per IEC
26 | Main terminal bushings, RIS |  | RIP & RIS Bushings
26.1 | Impulse withstand test voltage at sea level (1,2/50 ms)
26.1.1 | Primary | kV peak | 1050
26.1.2 | Secondary | kV peak | 350
26.1.3 | Tertiary | kV peak | 170
26.1.4 | Primary/Secondary Neutral | kV peak | 170
26.2 | Sixty-second, power-frequency withstand test voltage to earth
26.2.1 | Primary | kV r.m.s | 460
26.2.2 | Secondary | kV r.m.s | 140
26.2.3 | Tertiary | kV r.m.s | 70
26.2.4 | Primary/Secondary Neutral | kV r.m.s | 70
26.3 | Total creepage distance
26.3.1 | Based on: | mm/kV | 31
26.3.2 | Primary | mm | xxxxxxxxxx
26.3.3 | Secondary | mm | xxxxxxxxxx
26.3.4 | Tertiary | mm | xxxxxxxxxx
26.3.5 | Primary/Secondary Neutral | mm | xxxxxxxxxx
26.4 | Protected creepage distance
26.4.1 | Primary | mm | As per IEC
26.4.2 | Secondary | mm | As per IEC
26.4.3 | Tertiary | mm | As per IEC
26.4.4 | Primary/Secondary Neutral | mm | As per IEC
26.5 | Type, ratings and dimensions (attach data sheets) |  | Yes
26.5.1 | Service bushings stem dimensions
26.5.1.1 | Primary |  | 38 mm Dia, 125 mm long
26.5.1.2 | Secondary |  | 26 mm Dia, 125 mm long
26.5.1.4 | Tertiary |  | 26 mm Dia, 125 mm long
26.5.1.5 | Neutral |  | 26 mm Dia, 125 mm long
26.5.2 | Test bushings |  | N/A
26.5.3 | Give particulars of special turrets etc. that will be used |  | xxxxxxxxxx
26.5.4 | Special test items be supplied as part of the contract
26.5.5 | Special test agreed to:
26.5.4.1 | Accoustic noise as part of contract |  | Yes
26.5.4.2 | 1 hour over excitation test 1.12p.u as part of the contract |  | Yes
27 | Transformer general information
27.1 | Manufacturer |  | xxxxxxxxxx
27.2 | Place of manufacture |  | xxxxxxxxxx
27.3 | Type of transformer |  | Core
28 | Oil quantities:
28.1 | Transformer tank | m³ | xxxxxxxxxx
28.2 | Radiator | m³ | xxxxxxxxxx
28.3 | Conservator tank | m³ | xxxxxxxxxx
28.4 | Tap-changer | m³ | xxxxxxxxxx
28.5 | Total | m³ | xxxxxxxxxx
29 | Masses:
29.1 | Mass of core and windings | kg | xxxxxxxxxx
29.2 | Mass of core steel | kg | xxxxxxxxxx
29.3 | Mass of winding copper (insulation excluded) | kg | xxxxxxxxxx
29.4 | Mass of tank and fittings | kg | xxxxxxxxxx
29.5 | Mass of coolers incl. Pipes and supports | kg | xxxxxxxxxx
29.6 | Mass of oil | kg | xxxxxxxxxx
29.7 | Total mass | kg | xxxxxxxxxx
29.8 | Greatest transportation mass | kg | xxxxxxxxxx
30 | Filling medium for transport |  | Dry Air/ Oil
31 | Overall dimensions of tank only :
31.1 | Length | mm | xxxxxxxxxx
31.2 | Base plate thickness | mm | xxxxxxxxxx
32 | Transport dimensions:
32.1 | Length | mm | xxxxxxxxxx
32.2 | Width | mm | xxxxxxxxxx
32.3 | Height | mm | xxxxxxxxxx
32 | Height over Primary bushings |  | xxxxxxxxxx
33 | Tank and cooler material thickness:
33.1 | Tank - sides/ top/ bottom | mm | xxxxxxxxxx
33.2 | Cooler tubes | mm | xxxxxxxxxx
33.3 | Pressed-sheet radiators | mm | xxxxxxxxxx
33.4 | Hot dipped galvanised - no paint | mm | > 70 microns average
34 | Safe withstand vacuum at sea level | kPa | full vacuum
35 | On-load tap-changers
35.1 | Type and design: |  | MR
35.1.1 | Manufacturer and type designation |  | VacuuTap
35.1.2 | Precise electrical location of tappings |  | Primary End
35.2 | Tapping range of Primary/Secondary ratio % of the ratio on the principal tapping:
35.2.1 | Max | % | 105%
35.2.2 | Min | % | 85
35.2.3 | Number of steps | no. | 16
35.2.4 | Size of steps | % | 1.25
35.2.5 | Reversing/ Linear Switch/Coarse-fine |  | xxxxxxxxxx
35.2.5 | Number of positions (including transition positions) |  | 17
35.3 | Nominal 50 Hz ratings of tap-changer:
35.3.1 | Voltage | kV | To comply with IEC
35.3.2 | Current | A | To comply with IEC
35.3.3 | Temporary over voltages |  | 1.05 Um for 5 min
1.25 Um for 5 Seconds
1.5 Um for 1 second
1.75 Um for 0.25 seconds
36.4 | Insulation levels of tap-changer:
36.4.1 | Lightning impulse level (1,2/50 ms full wave) |  | To comply with IEC
36.4.2 | phase-to-ground | kV peak | To comply with IEC
36.4.3 | phase-to-phase | kV peak | To comply with IEC
36.5 | Tap-changer 50 Hz withstand:
36.5.1 | phase-to-ground | kV peak | To comply with IEC
36.5.2 | phase-to-phase | kV peak | To comply with IEC
36.5.3 | Nominal voltage and current rating of tap-changer |  | To comply with IEC
36.6 | Tap-changer contacts:
36.6.1 | Selector | kV/A | xxxxxxxxxx
36.6.2 | Selector switch | kV/A | xxxxxxxxxx
36.6.3 | Diverter switch | kV/A | xxxxxxxxxx
36.7 | Tap-changer transition resistor | kV/A | xxxxxxxxxx
36.8 | Tap-changer driving motor:
36.8.1 | Type of driving motor 3 Phase |  | 400VAC
36.8.2 | Power | kW | xxxxxxxxxx
36.8.3 | Current | A | xxxxxxxxxx
36.8.3 | Motor Voltage | VAC | xxxxxxxxxx
36.8.4 | Control voltage | VDC | 110
37 | Resulting no-load voltage appearing:
37.8.1 | On principal tapping | kV | 220
37.8.2 | On extreme plus tapping | kV | 231
37.8.3 | On extreme minus tapping | kV | 187
38 | Supply of contract drawings |  | Yes
39 | Type test certificates shall be submitted with the tender for approval, otherwise it will be assumed that no type tests for identical units are available |  | Yes
40 | Indicating and protective devices:
40.1 | Winding temperature thermometer(s) |  | Mesko with remote 4-20 milliamps signal, 3 pieces (Primary/Secondary/Tertiary). 6 required contacts per instrument.
40.2 | Oil temperature thermometer |  | Mesko with remote 4-20 milliamps signal, 3 pieces (Primary/Secondary/Tertiary). 6 required contacts per instrument.
40.3 | Rapid pressure relay - Quantity of 1 required |  | Qualitrol
40.4 | Oil- and gas-actuated relay |  | Cedaspe (As per specification)
40.5 | Pressure relief device |  | Qualitrol XPRD
40.6 | Tap-changer protective device (detail) |  | Yes
40.7 | Dehydrating breathers |  | Yes
40.8 | Conservator bag (Trelleborg or Pronal) |  | Yes
40.9 | Oil level indicators (Cedaspe) |  | Yes
40.10 | Gas monitor relay and conservator bags |  | Cedaspe
41 | Oil Specification |  | Nynas Nytro Libra SAGX/ Poweroil to 1020 (60UX)
42 | Special Requirements:
42.1 | Testing: Heat run test as per IEC to be performed on all units – overload testing at 130% for 1 hour to be performed during heat run. – Acceptance criteria will be as per IEC loading guide 60076-7 – long term emergency loading. In accordance with IEC – latest version as per contract date. |  | Yes
42.2 | Dielectric test to be performed as per relevant IEC standard. |  | Yes
42.3 | In accordance with IEC – latest version as per contract date, routine test specification – manufacturers routine test certificate will be provided for all results for individually supplied units, type test certificates will be accepted for all type tests on similar units. |  | Yes
42.4 | A number of separate SFRA tests must be done. The first test must be done without the bushings and oil and the second test with the oil and bushings at the manufacturer’s works. Another SFRA test to be done without bushings and oil at the port of import and again on site before the transformer is offloaded onto the plinth. A final SFRA test must be done after the transformer is installed, the bushings fitted and the transformer filled with oil; ready for testing and commissioning. This SFRA test must be done before any DC insulation tests. At no point should any DC insulation tests be done before an SFRA test. |  | Yes
42.5 | The dry film thickness of the paint should be at average 250 microns. The Contractor can submit alternative specification to the Employer for acceptance. |  | Yes
42.6 | Primary bushing test tap to face inwards and oil level gauge to face outwards |  | Yes
42.7 | Bucholzs Relays to be fitted with 10-mm copper sample pipe only from the top of the Bucholzs with needle and seat valve only. No gas sampling device. |  | Yes
42.8 | Core and clamps to be earthed separately by external bushings and labelled accordingly. |  | Yes
42.9 | For storage conditions, test bushings to be installed. |  | Not applicable
42.10 | Units must be painted in the following colour: RAL7035; Conservator tank to be painted RAL9010 |  | Yes
42.11 | Fiber optic sensors to be fitted on all units |  | Yes
42.12 | Copper Conductors to be varnished |  | Yes
42.13 | Short circuit test results of similar unit or design calculations |  | Yes
42.14 | All oil supplied must pass the IEC 62535 for corrosive sulphur |  | Yes
43 | Factory Tests
43.1 | Main test required as per IEC:
43.1.1 | Temperature rise test |  | See Annexure B for details
43.1.2 | Short time heat run test |  | See Annexure B for details
43.1.3 | Short circuit test |  | See Annexure B for details
43.1.4 | Lightning impulse test |  | See Annexure B for details
43.1.5 | Switching Impulse test |  | See Annexure B for details
43.1.6 | Induced over voltage test |  | See Annexure B for details
43.1.7 | Chopped impulse test |  | See Annexure B for details
43.1.8 | Accoustic noise level measurement |  | See Annexure B for details
43.1.9 | Overload test |  | See Annexure B for details
43.1.10 | Dielectric loss angle test and capacitance (Doble instrument) |  | See Annexure B for details
43.1.11 | Vibration test |  | See Annexure B for details
43.1.12 | SFRA ( Doble instrument) |  | See Annexure B for details
43.2 | Special tests: |  | See Annexure B for details
43.2.1 | 1 hour over excitation test 1.12 p.u |  | See Annexure B for details
43.2.2 | Infrared Scanning |  | See Annexure B for details
43.3 | Any other test
44 | Agreements on clarifications and deviations:
44.16.1 | Tertiary winding to be suitably rated to witstand short circuits but may only be loaded to 5MVA. Details to be provided on nameplate. |  | Yes
44.16.2 | Bushings to be fitted with shock indicators for transport purposes |  | Yes
44.16.3 | Core to be fitted with shock indicators for transport purposes |  | Yes
44.16.4 | Unit will be equipped with Sergi Protection system |  | Yes
44.16.5 | Maintenance free breather system to be installed (MR) |  | No
44.16.6 | Valves and mounting brackets to be installed for Drykeep and Drykeep to be fitted on site before commissioning. |  | No
44.16.7 | On-line gas analyser, Kelman type Transfix, to be fitted on the unit during site installation |  | No
44.16.8 | On-line tap changer monitoring(MR Reinhausen) |  | No
44.16.9 | Magnetisation of the curve of core |  | Yes Supply Curve
45 | Transport
45.1 | Make of Impact Recorders |  | Type RD298 ShockLog
46 | Technical information required for tender evaluation:
46.1 | Core design:
46.1.1 | Core sheet material
46.1.2 | Method of joints
46.1.3 | Number of limbs / wound limbs
46.1.4 | Core diameter | mm
46.1.5 | Window height | mm
46.1.6 | Centre leg distance main limb – main limb | mm
46.1.7 | Centre leg distance main limb – return limb | mm
46.1.8 | Cross section of wound limbs | m²
46.1.9 | Cross section of yoke between wound limbs | m²
46.1.10 | Cross section of unwound limbs | m²
46.2 | Total core mass: | kg
46.2.1 | Flux density in wound limbs | Tesla
46.2.2 | Flux density in yoke between wound limbs | Tesla
46.2.3 | Flux density in unwound limbs | Tesla
46.2.4 | Volt per turn at the above wound limb flux density | V
46.3 | Winding design:
46.3.1 | Provide a cross-sectional diagram of the windings showing relative position to the core
46.3.2 | Provide from each winding the following information:
46.3.3 | Wound limb
46.3.3.1 | Exciting Winding (next to the core)
46.3.3.2 | Type of winding (layer, helical, disk, interleaved disk, inter-shielded disk)
46.3.3.3 | Number of turns
46.3.3.4 | Inner diameter | mm
46.3.3.5 | Outer diameter | mm
46.3.3.6 | Radial build | mm
46.3.3.7 | Electrical height | mm
46.3.3.8 | Magnetic height | mm
46.3.3.9 | Conductor size, number and configuration | mm
46.3.3.10 | Conductor insulation | mm
46.3.3.11 | Current density | A/mm²
46.3.3.12 | Gradient winding - oil | °C
46.3.3.13 | Total copper mass | kg
46.4 | PW Winding
46.4.1 | Type of winding (layer, helical, disk, interleaved disk, inter-shielded disk)
46.4.2 | Number of turns
46.4.3 | Inner diameter | mm
46.4.4 | Outer diameter | mm
46.4.5 | Radial build | mm
46.4.6 | Electrical height | mm
46.4.7 | Magnetic height | mm
46.4.8 | Conductor size, number and configuration | mm
46.4.9 | Conductor insulation | mm
46.4.10 | Current density | A/mm²
46.4.11 | Gradient winding - oil | °C
46.4.12 | Total copper mass | kg
46.5 | SW Winding
46.5.1 | Type of winding (layer, helical, disk, interleaved disk, inter-shielded disk)
46.5.2 | Number of turns
46.5.3 | Inner diameter | mm
46.5.4 | Outer diameter | mm
46.5.5 | Radial build | mm
46.5.6 | Electrical height | mm
46.5.7 | Magnetic height | mm
46.5.8 | Conductor size, number and configuration | mm
46.5.9 | Conductor insulation | mm
46.5.10 | Current density | A/mm²
46.5.11 | Gradient winding - oil | °C
46.5.12 | Total copper mass | kg
46.6 | Regulating Winding
46.6.1 | Type of winding (layer, helical, disk, interleaved disk, inter-shielded disk)
46.6.2 | Number of turns
46.6.3 | Inner diameter | mm
46.6.4 | Outer diameter | mm
46.6.5 | Radial build | mm
46.6.6 | Electrical height | mm
46.6.7 | Magnetic height | mm
46.6.8 | Conductor size, number and configuration | mm
46.6.9 | Conductor insulation | mm
46.6.10 | Current density | A/mm²
46.6.11 | Gradient winding - oil | °C
46.6.12 | Total copper mass | kg
46.7 | Tertiary Winding
46.7.1 | Type of winding (layer, helical, disk, interleaved disk, inter-shielded disk)
46.7.2 | Number of turns
46.7.3 | Inner diameter | mm
46.7.4 | Outer diameter | mm
46.7.5 | Radial build | mm
46.7.6 | Electrical height | mm
46.7.7 | Magnetic height | mm
46.7.8 | Conductor size, number and configuration | mm
46.7.9 | Conductor insulation | mm
46.7.10 | Current density | A/mm²
46.7.11 | Gradient winding - oil | °C
46.7.12 | Total copper mass | kg
NOTES:
1 | At the radial upper and lower of the PW and SW end different conductor sizes to minimize the eddy current losses due to the radial stray flux
2 | All twin and triple conductors are with additional enamel insulation of the single strips. Therefore these conductors are corrosive sulphur proof as well as the single strips of the CTC
3 | The CTC as well as the twin and triple conductors are low chip epoxy bounded.
4 | Short circuit calculation on extreme plus/principal/extreme minus tap with 100%/105%/110% excitation

## Schedule B
Section 27 Schedule B: EQUIPMENT/MATERIAL SUPPLIERS
Item | Material/Equipment | Designation and Type | Manufacturer | Country of Manufacturer | Designation and Type | Manufacturer | Country of Manufacturer
|  | Requirements |  |  | Offered
1 | Bushings | Resin Impregnated Paper, with silicone sheds | ABB Micafil | Switzerland
|  |  | ABB Ludvika | Sweden
2 | On-load Tap Changers | xxxxxxxxxx | MR Vacuum Tap | Germany
|  |  | VUCG Type | Ludvika, Sweden
3 | Bucholtz Relay | EE Series | Cedaspe | Italy
4 | Conservator Bag Leak Detector | CPR 3 | Cedaspe | Italy
5 | Oil level indicators | NPG Series | Cedaspe | Italy
6 | Winding temperature indicators | With transmitter 4 – 20 mA for remote indication | AKM or Messko | Sweden
7 | Oil temperature indicators | With transmitter 4 – 20 mA for remote indication | AKM or Messko | Sweden
8 | Conservator bags | xxxxxxxxxx | Trelleborg | Sweden
|  |  | Pronal | France
9 | Maintenance Free Silica-gel breather | MTraB | MR | Germany
10 | Pressure Relief Device | XPRD | Qualitrol | USA
11 | Sudden Pressure Relay | 900/910 Series | Qualitrol | USA
12 | Protective Relay For OLTC | RS - 2001 | MR | Germany
13 | Radiators | Hot dipped galvanised, at least 65 microns without painting | xxxxxxxxxx | xxxxxxxxxx
14 | Cooling Fan & Motor | xxxxxxxxxx | Krenz | USA
|  |  | California | USA
|  |  | Howden Safanco | RSA
|  |  | WEG | Brazil
15 | Terminal Blocks | xxxxxxxxxx | Entrelec spring loaded screw type | xxxxxxxxxx
|  |  | Phoenix spring loaded screw type | xxxxxxxxxx
16 | Cables – control and power | Steel wire armoured (SWA) | xxxxxxxxxx | xxxxxxxxxx
17 | Oil | Nynas Nytro Libra SA-GX (Inhibited) | NYNAS | Sweden
|  | Poweroil to 1020 (60UX) | Engen | RSA
18 | Fibre Optic Temperature Probes | xxxxxxxxxx | Neoptix | Canada
19 | Online Gas In Oil Analyser (DGA) | Calisto 9 | Morgan Shaffer | USA
|  | Severon TM8 | Severon/Qualitrol | USA
|  | Gas Guard 8 | Siemens | Germany
20 | Transformer Fire Protection | TP, TPA, TPB, and TPAB | SERGI | France

## Schedule C
Section 27 Schedule C: DEVIATIONS FROM TECHNICAL AND COMMERCIAL REQUIREMENTS
Clause / Section | Proposed Deviation | Reason

## Schedule D
Section 27 Schedule D: Guaranteed Delivery Dates
No Of Units | Site Location (Delivery) | Guaranteed Delivery Date
1 | Brakwater Depot